Deriving the Smax Algorithm
for Non-unity Power Factors

# Overview
The maximum feed-in for a photovoltaic system (PV) to be installed at a customer location is desired. Each location is calculated separately, assuming no other PV systems are connected. The simple calculation for feed-in for unity power factor is not applicable when the power factor is a constant but non-unity value.

# Given
At the location under test, the supplied PV power is:
S = S_{max}cos{%phi} + S_{max}sin{%phi}j = v_{c} times i rSup {"*"}	(1)
where S_{max} is the apparent power, ϕ is the power factor angle pf = cos(%phi) and i rSup{ "*"} is the complex conjugate of the current.
The limiting voltage is normally a maximum of 3% over the nominal, a factor we can call k. The SWING voltage is assumed to be all real, i.e. vn = vre + 0j. Then:
abs{ v_{c}} leslant ( 1 + threshold ) v_{n} = kv_{ n}
This complex voltage can be expressed as a function of the unknown voltage phasor (a function of angle %theta ) at the node under test:
v_{c} = kv_{n}( cos({%theta}) + sin({%theta})j)
## Derivation
The current is calculated as the voltage difference divided by the complex impedance:
i = v_%DELTA over Z = {v_{c} - v_{n}} over Z = {kv_{ n}( cos{%theta} + sin{%theta}j) - v_{n}} over Z = v_{ n}( (kcos{%theta} -1) + ksin{%theta}j) times (g + bj)
by using admittance:
1 over Z = 1 over {r+xj} = r over { r^2 + x^2 } - x over { r^2 + x^2 }j = r over {abs{Z}}^2 - x over {{abs{Z}}^2}j = g+bj = Y
Expanding:
i = v_{ n} [(kcos{%theta} g - ksin{%theta} b - g) + (kcos{%theta} b - ksin{%theta} g)j ]
Then
S = v_{c} times i rSup {"*"} = kv_{n}( cos({%theta}) + sin({%theta})j) times v_{ n} [(kcos{%theta} g - ksin{%theta} b - g) - (kcos{%theta} b - ksin{%theta} g)j ] newline {} = kv_{ n}^2[ ( kg - cos{%theta}g - sin{%theta}b) + (-kb + cos{%theta}b - sin{%theta}g)j ]	(2)

Equating real and imaginary parts of (1) and (2):
S = S_{re} + S_{im}j = S_{max}cos{%phi} + S_{max}sin{%phi}j = kv_{ n}^2[ ( kg - cos{%theta}g - sin{%theta}b) + (-kb + cos{%theta}b - sin{%theta}g)j ] newline S_{max}cos{%phi} = kv_{ n}^2( kg - cos{%theta}g - sin{%theta}b ) newline S_{max}sin{%phi} = kv_{ n}^2(-kb + cos{%theta}b - sin{%theta}g) newline S_{max} = kv_{ n}^2( kg - cos{%theta}g - sin{%theta}b ) over {cos{%phi}} newline S_{max} = kv_{ n}^2(- kb + cos{%theta}b - sin{%theta}g) over {sin{%phi}} newline equating: newline kv_{ n}^2( kg - cos{%theta}g - sin{%theta}b ) over {cos{%phi}} = kv_{ n}^2(- kb + cos{%theta}b - sin{%theta}g) over {sin{%phi}} newline ( kg - cos{%theta}g - sin{%theta}b ) over {cos{%phi}} = (- kb + cos{%theta}b - sin{%theta}g) over {sin{%phi}} newline tan{ %phi } = (- kb + cos{%theta}b - sin{%theta}g) over ( kg - cos{%theta}g - sin{%theta}b ) newline %phi = arctan[(- kb + cos{%theta}b - sin{%theta}g) over ( kg - cos{%theta}g - sin{%theta}b ) ] newline newline alignl {as terms of S} newline newline widetilde {S_{re}} = S_{re} over {kv_n}^2 = (- kb + cos{%theta}b - sin{%theta}g) newline widetilde {S_{im}} = S_{im} over {kv_n}^2 = ( kg - cos{%theta}g - sin{%theta}b )newline %phi = arctan(widetilde {S_{im}} over widetilde {S_{re}}) newline	(3)
## Solving
Solving the final non-linear equation in (3) for the unknown θ, has no obvious closed form solution. Instead we perform a non-linear optimization to find the voltage phasor angle θ, that minimizes, the difference between the left and right hand sides:
f( %theta ) = (arctan(widetilde {S_{im}} over widetilde {S_{re}}) - %phi )^2 = (arctan[u(%theta)] - %phi )^2 = ( arctan[(- kb + cos{%theta}b - sin{%theta}g) over ( kg - cos{%theta}g - sin{%theta}b ) ] - %phi )^2	(4)
We choose to square the difference to avoid problems with differentiability of an absolute value function.
## Partial Derivatives
To perform the optimization using Newton's method, we require the first and second partial derivatives of the function. So, using:
{partial atan({a})} over {partial x} = {1 over {1 + a^2}} cdot {{partial a} over {partial x}} newline {partial a over b} over {partial x} = {{{partial a} over {partial x}}b - a {{partial b} over {partial x}}} over b^2 = { 1 over b }{{partial a} over {partial x}} - { a over b^2 }{{partial b} over {partial x}}
the derivative is:
{partial f(%theta)} over {partial %theta} = 2( arctan[u(%theta)] - %phi ) cdot {{partial arctan[u(%theta)]} over {partial %theta}} = 2( arctan[u(%theta)] - %phi ) cdot {1 over { 1 + u(%theta)^2} cdot {{partial u(%theta)} over {partial %theta}}}
where

{partial u(%theta)} over {partial %theta} = {partial widetilde {S_{im}} over widetilde {S_{re}}} over {partial %theta} = {} { 1 over widetilde {S_{re}}}{{partial widetilde {S_{im}}} over {partial %theta}} - { widetilde {S_{im}} over widetilde {S_{re}}^2}{partial widetilde {S_{re}}} over {partial %theta} = {} newline { 1 over widetilde {S_{re}}}(-sin{%theta}b - cos{%theta}g) - { widetilde {S_{im}} over widetilde {S_{re}}^2}(sin{%theta}g - cos{%theta}b )

Finally
{partial f(%theta)} over {partial %theta} = 2( atan[widetilde {S_{im}} over widetilde {S_{re}}] - %phi ) cdot {1 over { 1 + ({widetilde S_{im}} over widetilde S_{re})^2}} cdot (-sin{%theta}b - cos{%theta}g) - { widetilde {S_{im}} over widetilde {S_{re}}^2}(sin{%theta}g - cos{%theta}b )